Controller / MTB / MTB

BNS-MTB - (102148979)

INOTEC monitoring device BNS-MTB

Fully automated, microprocessor controlled test facility acc. to DIN VDE V 0108-100-1, part 1, paragraph 6.4.3.10, for programming and monitoring of maximum 64 INOTEC self-contained luminaires with SV function control (additional 64 INOTEC self-contained luminaires connectable as an option).

Serial data bus via a 2-wire unshielded data line, for example YR 2x0,8mm²

Programming and monitoring functions:
-	Automatic weekly function test of all connected single-battery luminaires
-	Annual battery duration test
-	Continuous charging control

The results of all executed tests are shown with date and time via real-time clock on an OLED-graphic-display in plain text, for example:
- 	Destination of each luminaire
- 	Correct function of all luminaires or analytic failure messages of the following:
-	Charging failure
-	Luminaire defect
-	Communication failure
-	Results of the last batter duration test in minutes until deep discharge protection of each luminaire is activated
-	Registering of all power failures showing the fault detections

Following features are included as standard:
- 	OLED-graphic-display
- 	Operation via comfortable rotary switch
- 	All the test results of the last 2 years are saved automatically and available at any time
- 	PS/2-terminal for standard keypad for a simplified programming of the system
- 	4 volt-free contacts (operation, battery operation, failure operation and optional)
- 	Buzzer with acoustic report

Optional features:
- 	Further BUS-terminal for additional connection of up to 64 INOTEC self-contained luminaires
- 	or RTG-module for connection with monitoring software INOView
- 	or INOLan-module for connection with monitoring software INOView
- 	or INOWeb-module for monitoring purposes via a standard web browser

Protection category: IP20
Protection class: I
Rated voltage: 230V AC ±10% 50/60 Hz
Permitted temperature range: -5...+30 °C

Made in Germany

Brand: INOTEC Sicherheitstechnik GmbH