DER- luminaires / Wall, floor and stair luminaire / FS 1100

FS 1100 TE LED 48V RAL 7015  - (101234755)

Dynamic Escape Route luminaire FS 1100TE D.E.R. 48V  RAL 7015

Dynamic Escape Route luminaire for floor installation, including run light functionality.  Ideal to display the safe escape route depending on the smoke situation inside a building. Power supply by PSU 48.
Luminaire only for indoor installation! 

The following characteristics need to be complied with:

Zweikanaliger LED-Treiber mit integrierter Einzelleuchtenüberwachung. Hohe Funktionssicherheit durch Einhaltung internationaler Standards zur Sicherheit und Arbeitsweise, elektromagnetische Verträglichkeit und Störsicherheit. Zum Anschluss an INOTEC SEV oder SEV-A.

- Mounting type: flush carpet installation
- Material: stainless steel
- Dim.: Diameter: 136 mm
- Mounting depth: 74 mm
- Input terminal: 1.5mm²

- Illuminant: 4 x 1W LED-module
- Service life: 50.000 h

- Protection category: IP65
- Protection class: III
- Rated voltage: 48 V DC +/-10 %
- Power consumption battery operation: 35 mA
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.
10-years of resupply guarantee for compatible LED-modules and wear parts

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.