System luminaires / Straight-Line / SNP 1530.1

SNP 1530.1 D / WA LED J/SV,RAL 9016 - (101253347)

Escape sign luminaire SNP 1530.1D/WA LED J/SV  RAL 9016

Straight-Line high quality emergency exit luminaires, made of powder coated aluminium profile of just 14.5mm thickness. Slim design and brilliant illumination by cutting-edge fibre optics technology with a luminance of >500cd/m². 

The following characteristics need to be complied with:

LED-driver with integrated individual lamp monitoring for stand-by and continuous lighting without seperate BUS-line. Complying with international standards for safety and working, electromagnetic compatibility and interference resistance. LED output dimmable continuously in mains operation. For connection to JOKER-central battery systems.

- viewing distance: 30 m

- Mounting type: wall bracket or ceiling mounting
- Material: aluminium powder-coated
- Dim.: Length x Width x Height: 337 mm x 236 mm x 50 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: 18 x 0,1W LED-module
- Light colour: 6500 K
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP40
- Protection class: I
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 18 mA
- Apparent power: 5,2 VA
- Inrush current: 8 A / 50 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.

paror equivalent and ready for use.