System luminaires / Straight-Line / SNP 1530.1

SNP 1530.1 P LED NE/SV RAL 9016   - (101254862)

Escape sign luminaire SNP 1530.1P LED NE/SV  RAL 9016

Straight-Line high quality emergency exit luminaires, made of powder coated aluminium profile of just 14.5mm thickness. Slim design and brilliant illumination by cutting-edge fibre optics technology with a luminance of >500cd/m². 

The following characteristics need to be complied with:

LED-driver with integrated individual lamp monitoring for non-maintained, maintained lighting with seperate BUS-line. Permanent monitoring of maintained luminaires. In case of an interruption of the data line the luminaires are turned on independent of the operating status! Complying with international standards for safety and working, electromagnetic compatibility and interference resistance for high function safety. LED output dimmable continuously in mains operation. For connection to INOTEC-NEA-monitoring systems.

- viewing distance: 30 m

- Mounting type: pendulum mounting
- Material: aluminium powder-coated
- Dim.: Length x Width x Height: 337 mm x 187 mm x 54 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: 18 x 0,1W LED-module
- Light colour: 6500 K
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP40
- Protection class: I
- Rated voltage: 230 V AC +/-10 % 50/60 Hz
- Apparent power: 5,3 VA
- Inrush current: 8 A / 50 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.