System luminaires / EX - Luminaires / EX 7102

EX 7102 LED J/SV - (101284366)

Safety- and emergency sign luminaire EX 7102 LED J/SV  

Ex-safety- /exit-luminaire for zone 1, 2, 21, 22. Made of high-quality glass fiber reinforced polyester resin for wall or ceiling mounting.
EU-Baumusterprüfbescheinigung: IBExU 17 ATEX 1132
Explosionsschutz
II 2 G Ex eb mb op is q IIC T4 Gb (Zone 1)
II 2 G Ex db eb mb op is q IIC T4 Gb (Zone 1)
II 2 D Ex op is tb IIIC T80°C Db (Zone 21). 

The following characteristics need to be complied with:

LED-driver with integrated individual lamp monitoring without seperate BUS-line. Complying with international standards for safety and working, electromagnetic compatibility and interference resistance.

- viewing distance: 30 m

- Mounting type: wall or ceiling mounting
- Material: polyester, polycarbonate
- Dim.: Length x Width x Height: 226 mm x 460 mm x 152 mm

- Illuminant:  LED-module
- Light colour: 6500 K
- Service life: 80.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP66
- Protection class: I
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 25 mA
- Apparent power: 6,5 VA
- Inrush current: 35 A / 95 µs
- Permitted temperature range: -30...+50 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.

paror equivalent and ready for use.