System luminaires / Downlights / SN 8400

SN 8400 -03 SLB LED J/SV SQ RAL 9016   - (101301645)

Safety luminaire SN 8400-03 SLB LED J/SV square RAL 9016

LED safety luminaire with optimised light distribution for the illumination of small areas such as lavatories or electrical operating rooms with a luminaire. Housing made of powder-coated aluminium for ceiling mounting with optional cable entry at the side.

Light distribution: Symmetric Low Bay for the illumination of areas. For mounting heights up to: 5,0 m. maximum 8,6 m luminaire distance for area illumination with 1 lx according to EN 1838, taking into account a maintenance factor of 0.8.

Incl. 4-chip LED illuminant for maximum safety. 

The following characteristics need to be complied with:

LED-driver with integrated individual lamp monitoring for stand-by and continuous lighting without seperate BUS-line. Complying with international standards for safety and working, electromagnetic compatibility and interference resistance. LED output dimmable continuously in mains operation. For connection to JOKER-central battery systems.
Auswechselbares Betriebsgerät zur vereinfachten Wartung und Instandhaltung.

- Mounting type: ceiling mounting
- Material: die-cast aluminum powder-coated
- Panel shape: square
- Dim.: Length x Width x Height: 130 mm x 130 mm x 59 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: replaceable 1 x 0,9W LED-module
- Light colour: 4000 K
- Light distribution: Symmetric Low Bay
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP40
- Protection class: I
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 12 mA
- Apparent power: 3,5 VA
- Inrush current: 8 A / 50 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.