System luminaires / Downlights / SN 8500

SN 8500-25 LED J/SV/S IP65HWF 9006 - (101302857)

Safety luminaire SN 8500-25 LED J/SV/S  HWF 9006

Downlight for enhanced lighting requirements. For illuminating workplaces with special risks, swimming pools or sports facilities. Robust, chlorine-resistant housing made of die-cast aluminium with optional lateral cable gland.

Ball-impact and shock resistant safety luminaires tested acc. to DIN VDE 0710-13.

Luminaires without testing acc. to DIN VDE 0710-13 as well as luminaires wih ball impact guards are not approved. According test certificates need to be added to the offer. 

The following characteristics need to be complied with:

LED-Betriebsgerät und Überwachngsmodul mit Einzelleuchtenüberwachung und frei programmierbarer Schaltungsart für Bereitschaftslicht (BL) und Dauerlicht (DL) ohne separate Busleitung. Hohe Funktionssicherheit durch Einhaltung internationaler Standards zur Sicherheit und Arbeitsweise, elektromagnetische Verträglichkeit und Störsicherheit. Zum Anschluss an JOKER-Zentralbatterieanlagen. LED driver with active power factor correction (PFC) to reduce reactive power in mains operation. For connection to JOKER-central battery systems.

Luminaire with integrated 230V switch input for switched maintained operation or local phase monitoring function.

- Mounting type: ceiling mounting
- Material: die-cast aluminum
- Dim.: Length x Width x Height: 173 mm x 328 mm x 72 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: 1 x 25W LED-module
- Light colour: 4000 K
- Light distribution: Symmetric High Bay, Symmetric Low Bay
- Service life: 50.000 h

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP65
- Protection class: I
- Impact resistance: IK10
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 135 mA
- Apparent power: 30,9 VA
- Inrush current: 11 A / 264 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.

paror equivalent and ready for use.