System luminaires / Downlights / SN/A 8727

SN/A 8727 LED J/SV 4K RAL 9010 - (101308618)

Safety and general lighting SN/A 8727 LED J/SV  RAL 9010

Shapely round luminaire with a PMMA dome, for universal use in safety and general lighting. The luminaire is optionally available with motion detector. 

Operating values for general lighting (without safety lighting): 
apparent power: 33VA 
active power: 32W 

The following characteristics need to be complied with:

LED-driver with integrated individual lamp monitoring for stand-by and continuous lighting without seperate BUS-line. Complying with international standards for safety and working, electromagnetic compatibility and interference resistance. LED output dimmable continuously in mains operation. For connection to JOKER-central battery systems.
Auswechselbares Betriebsgerät zur vereinfachten Wartung und Instandhaltung.

- Mounting type: wall or ceiling mounting
- Material: PMMA
- Dim.: Diameter: 460 mm, Height: 95 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: replaceable 12 x 0,3W + 70 x 0,3W LED-module
- Light colour: 4000 K
- Light distribution: Symmetric High Bay, Symmetric Low Bay
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP40
- Protection class: I
- Impact resistance: IK04
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 36 mA
- Apparent power: 8,6 VA
- Inrush current: 8 A / 50 µs
- Permitted temperature range: -15...+30 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.