System luminaires / Downlights / SN 9400

SN 9400 -03 SLB LED RD RAL 9016   - (101325186)

Safety luminaire SN 9400-03 SLB LED 24V round RAL 9016

LED safety luminaire with optimised light distribution for the illumination of small areas such as lavatories or electrical operating rooms with a luminaire. Recessed ceiling luminaires with powder-coated aluminium trim without visible screws. Tool-less installation in Ø 68mm ceiling cutout. Delivery incl. installed LED-driver in installation casing for recessed ceiling-mounting with strain relief for a tool-free mounting.

Light distribution: Symmetric Low Bay, for the illumination of areas. For mounting heights up to: 5,0 m. maximum 8,6 m luminaire distance for area illumination with 1 lx according to EN 1838, taking into account a maintenance factor of 0.8.

Incl. 4-chip LED illuminant for maximum safety. 

The following characteristics need to be complied with:

LED driver with integrated single LED monitoring for detection of individual defect LEDs at short circuit or open circuit. Freely programmable non-maintained (BL) and maintained (DL) operation for each individual luminaire without additional data line. Addressing with pre-programmed unique ID, no manual addressing. Luminaires individually switchable and dimmable via the emergency lighting system. High functional safety by compliance to international standards for safety and operation, electromagnetic compatibility and interference immunity. For connection to INOTEC systems with 24V circuits.

- Mounting type: recessed ceiling mounting
- Material: die-cast aluminum powder-coated
- Panel shape: round
- Dim.: Diameter: 88 mm, Height: 7 mm
- Ceiling cut-out diameter: 68 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: 1 x 0,9W LED-module
- Light colour: 4000 K
- Light distribution: Symmetric Low Bay
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP20, IP43
- Protection class: III
- Rated voltage: 24 V DC +/-20 %
- Power consumption battery operation: 65 mA
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.