System luminaires / Downlights / SN 8040 TES

SN 8040 TES 24V/S IP65 2K,RAL 9016 - (101354387)

Safety luminaire SN 8040 LED 24V/S  RAL 9016

Elegant high-quality LED downlight ideal for area or escape route illumination.  Perfect for combined usage of safety and general lighting. Possible adaption to the light colour of the general lighting by Translucent-Emitting-Surface (TES) technology. Powder-coated aluminium housing for ceiling mounting with high protection category and without any visible screws.

Rotationally symmetric light distribution with blinding due to a homogeneous light - emitting surface, ideal to illuminate areas and escape routes. For mounting heights up to 6,0m. According to EN 1838 considering the maintenance factor of 0,8, max. 11,7m lighting space of 1lx on the centre line of the escape route. 

The following characteristics need to be complied with:

LED driver with integrated single LED monitoring for detection of individual defect LEDs at short circuit or open circuit. Freely programmable non-maintained (BL) and maintained (DL) operation for each individual luminaire without additional data line. Addressing with pre-programmed unique ID, no manual addressing. Luminaires individually switchable and dimmable via the emergency lighting system. High functional safety by compliance to international standards for safety and operation, electromagnetic compatibility and interference immunity. For connection to INOTEC systems with 24V circuits.

Luminaire with integrated 230V switch input for switched maintained operation or local phase monitoring function.

- Mounting type: ceiling mounting
- Material: aluminium powder-coated
- Dim.: Diameter: 106 mm, Height: 130 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: 4 x 1W LED-module
- Light distribution: Symmetric High Bay, Symmetric Low Bay
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP65
- Protection class: I
- Rated voltage: 24 V DC +/-25 %
- Power consumption battery operation: 200 mA
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.

paror equivalent and ready for use.