System luminaires / Downlights / SN Line

SN LINE E-12 SHB FLD 230V,RAL 9010 - (101396827)

Safety luminaire SN LINEE-12 SHB FLD 230V  RAL 9016

LED safety luminaire with optimised light distribution for the illumination of areas. LED carrier for Trilux E-Line trunking system T5N/LED or T8. mounting to the trunking profile by means of stainless steel snap locks that can be applied tool-free. The design of the four snap locks allows visual inspection of the secure locking of the carrier to the profile. Carrier made of sheet steel. Automatic electrical connection by plug-in contacts with circuit selection. The circuit selection is done tool-less.

Light distribution: Symmetric High Bay, for the illumination of areas with high mounting heights. For mounting heights up to: 10,0 m. maximum 17,7 m luminaire distance for area illumination with 1 lx according to EN 1838, taking into account a maintenance factor of 0.8.

Incl. 4-chip LED illuminant for maximum safety. 

The following characteristics need to be complied with:

LED driver with integrated single LED monitoring for detection of defective LED in case of short-circuit or open circuit. Continuous monitoring of LED luminaires during maintained operation. Free configuration of each luminaire according to the requested operation mode in maintained, non-maintained or switched-maintained operation without the need of an additional data line. Each luminaire is switchable and dimmable via the control unit of the system. Including timer function to switch off or dim luminaires in battery mode to reduce the required lighting level (acc. to EN 12193) or in buildings with different rated duration times. Addressing with fixed ID without requirement of manual adjustment. High functional reliability due to the fulfillment of international standards for safety and operation, electromagnetic compatibility and immunity to interference. LED driver with active power factor correction (PFC) to reduce the reactive power in mains operation. For connection to FUSION central battery- or emergency power (NEA) systems.

- Mounting type: 07650...7LV+5LV Trilux E-Line
- Material: sheet steel painted
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: 1 x 3,5W LED-module
- Light colour: 4000 K
- Light distribution: Symmetric High Bay
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP20
- Protection class: I
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 25 mA
- Apparent power: 5,8 VA
- Inrush current: 6 A / 34 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.

paror equivalent and ready for use.