Self-contained luminaires / Wall, floor and stair luminaires / BN/V 6206

BN/V 6206 -11 LED IP65 RAL 9016   - (101405517)

Self-contained safety luminaire BN/V 6206-11 SV/B LED 1-8/D  RAL 9016

LED safety luminaire for illumination of escape routes and exit doors. Luminaire for wall mounting with high protection category and elegant housing made of powder coated aluminium without visible screws.

Suitable for the usage in outdoor areas due to an outsourced supply unit.

Self-monitoring self contained LED luminaires incl. high-quality high-temperature cells. 

The following characteristics need to be complied with:

External single battery supply unit for INOTEC BN/V LED luminaires.
LED-driver with integrated individual lamp monitoring for non-maintained, maintained and switched-maintained lighting. With integrated charging technology and freely selectable nominal operating time of 1h, 1,5h, 2h, 3h or 8h with INOTEC SV/B- function control to connect to a central monitoring device BNS-MTB according to EN 50172, DIN VDE 0100-718 and DIN VDE V 0108-100-1.
 Luminaire including test button for manual function and duration test with detailled LED status- and charge control indicator.
Complying with the international standards for safety and working, electromagnetic compatibility and interference resistance for high function safety. LED output dimmable continuously in mains operation.

- Mounting type: wall mounting
- Material: aluminium powder-coated
- Input terminal: max. 2,5mm² single-core

- Illuminant: 1 x 1W LED-module
- Light colour: 6500 K
- Service life: 50.000 h

- Protection category: IP65
- Protection class: II
- Rated voltage: 230 V AC +/-10 % 50/60 Hz
- Apparent power: 5,9 VA
- Inrush current: 11 A / 64 µs
- Permitted temperature range: M: -5...+35 °C, NM: 0...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.