DER- luminaires / Aluminium luminaires / FL 7288

FL 7288 K CLDD 230V - (101951141)

Dynamic emergency exit sign luminaire FL 7288K CLDD 230V  Aluminium

Dynamic double-sided emergency exit sign luminaire made of high quality aluminium profile. Ideal to display the safe escape route depending on the smoke situation inside a building.
For single-sided use, the current consumption is reduced by 50%. 

The following characteristics need to be complied with:

- viewing distance: 35 m

- Mounting type: chain mounting
- Material: aluminium
- Dim.: Length x Width x Height: 342 mm x 192 mm x 80 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant:  LED-module
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP40
- Protection class: I
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 44 mA
- Apparent power: 11,2 VA
- Inrush current: 6 A / 22 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.
10-years of resupply guarantee for compatible LED-modules and wear parts

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.