System luminaires / Downlights / SN 9024.1

SN 9024.1 -03 SLB LED RD RAL 9016   - (102476860)

Safety luminaire SN 9024.1-03 SLB LED 24V round RAL 9016

Discreet LED safety luminaire with optimised light distribution for the illumination of areas. Powder-coated aluminium cover with a diameter or edge length of no more than 45mm. Luminaire incl. driver for installation in ceiling cut-out of Ø 38mm.

Light distribution: Symmetric Low Bay, for the illumination of areas. For mounting heights up to: 5,0 m. maximum 8,6 m luminaire distance for area illumination with 1 lx according to EN 1838, taking into account a maintenance factor of 0.8. 

The following characteristics need to be complied with:

LED driver with integrated single LED monitoring for detection of defective LED in case of short-circuit or open circuit. Continuous monitoring of LED luminaires during maintained operation. Free configuration of each luminaire according to the requested operation mode in maintained, non-maintained or switched-maintained operation without the need of an additional data line. Each luminaire is switchable and dimmable via the control unit of the system. Addressing with fixed ID without requirement of manual adjustment. High function safety due to the compliance of international standards for safety and functioning, electromagnetic compatibility and interference resistance. For connection to INOTEC systems with 24V circuits.

- Mounting type: recessed ceiling mounting
- Panel shape: round
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: 1 x 0,9W LED-module
- Light colour: 4000 K
- Light distribution: Symmetric Low Bay
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP20, IP43
- Protection class: III
- Rated voltage: 24 V DC +/-25 %
- Power consumption battery operation: 80 mA
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.