System luminaires / Lichtbandleuchten / SN 8300 Maxos Fusion -12 SLB

SN 8300 Maxos fusion -12 SLB LED J/SV RAL 9003   - (104306726)

Safety luminaire SN 8300-12 SLB LED J/SV  RAL 9003

LED safety luminaire with optimised light distribution for the illumination of areas. Geräteträger für Maxos fusion und Maxos unifiy (LL5..T 4x2.5+8x1.5 Gen2 ..) Tragschiene. Einfaches Einclipsen mit Hilfe der werkzeuglos zu betätigenden Rastverschlüsse zur elektrischen Kontaktierung inkl. Stromkreisauswahl und mechanischen Befestigung.

Light distribution: Symmetric Low Bay for the illumination of areas. For mounting heights up to: 6,0 m. maximum 15,5 m luminaire distance for area illumination with 1 lx according to EN 1838, taking into account a maintenance factor of 0.8.

Incl. 4-chip LED illuminant for maximum safety. 

The following characteristics need to be complied with:

LED-driver with integrated individual lamp monitoring for stand-by and continuous lighting without seperate BUS-line. Complying with international standards for safety and working, electromagnetic compatibility and interference resistance. The LED output can be dimmed in two steps during mains operation. For connection to JOKER-central battery systems.
Replaceable power supply unit for easier maintenance and servicing.

- Mounting type: for installation in Signify Maxos fusion &amp; Maxos unify trunking rail 13 -cores
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: replaceable 4 x 1W LED-module
- Light colour: 4000 K
- Light distribution: Symmetric Low Bay
- Service life: 50.000 h

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection class: I
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 32 mA
- Apparent power: 8,3 VA
- Inrush current: 8 A / 50 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.