System luminaires / Wall, floor and stair luminaires / SN 6201

SN 6201 -06 LED 24V/S 3K IP65 RAL 7015   - (104360781)

Safety luminaire SN 6201-06 LED 24V/S  RAL 7015

Luminaire with targeted light output. Robust trapezoidal luminaire housing for wall mounting made of powder-coated die-cast aluminium. High protection rating for outdoor installation. And optional cable entry at the side. 

The following characteristics need to be complied with:

LED driver with integrated single LED monitoring for detection of individual defect LEDs at short circuit or open circuit. Freely programmable non-maintained (BL) and maintained (DL) operation for each individual luminaire without additional data line. Addressing with pre-programmed unique ID, no manual addressing. Luminaires individually switchable and dimmable via the emergency lighting system. High functional safety by compliance to international standards for safety and operation, electromagnetic compatibility and interference immunity. For connection to INOTEC systems with 24V circuits.

Luminaire with integrated 230V switch input for switched maintained operation or local phase monitoring function.
Auswechselbares Betriebsgerät zur vereinfachten Wartung und Instandhaltung.

- Mounting type: wall mounting
- Material: die-cast aluminum powder-coated
- Dim.: Length x Width x Height: 264 mm x 183 mm x 83 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: replaceable 18 x 0,3W LED-module
- Light colour: 3000 K
- Light distribution: Asymmetric Wall
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP65
- Protection class: I
- Impact resistance: IK09
- Rated voltage: 24 V DC +/-25 %
- Power consumption battery operation: 295 mA
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.