Self-contained luminaires / Wall, floor and stair luminaires / BN/V 6201

BN/V 6201 -03 LED IP65 3K RAL 7015   - (104366340)

Self-contained safety luminaire BN/V 6201-03 SV/B LED 1-8/D  RAL 7015

Luminaire with targeted light output. Robust trapezoidal luminaire housing for wall mounting made of powder-coated die-cast aluminium. High protection rating for outdoor installation. And optional cable entry at the side. Suitable for the usage in outdoor areas due to an outsourced supply unit. 
External supply unit: IP66; Ta: -5...+40 °C 

The following characteristics need to be complied with:

External single battery supply unit for INOTEC BN/V LED luminaires.
LED-driver with integrated individual lamp monitoring for non-maintained, maintained and switched-maintained lighting. With integrated charging technology and freely selectable nominal operating time of 1h, 1,5h, 2h, 3h or 8h with INOTEC SV/B- function control to connect to a central monitoring device BNS-MTB according to EN 50172, DIN VDE 0100-718 and DIN VDE V 0108-100-1.
 Luminaire including test button for manual function and duration test with detailled LED status- and charge control indicator.
Complying with the international standards for safety and working, electromagnetic compatibility and interference resistance for high function safety. LED output dimmable continuously in mains operation.

- Mounting type: wall mounting
- Material: die-cast aluminum powder-coated
- Dim.: Length x Width x Height: 264 mm x 183 mm x 83 mm
- Input terminal: max. 2,5mm² single-core

- Illuminant: 18 x 0,32W LED-module
- Light colour: 3000 K
- Service life: 50.000 h

- Protection category: IP65
- Protection class: III
- Impact resistance: IK09
- Rated voltage: 230 V AC +/-10 % 50/60 Hz
- Apparent power: 6,0 VA
- Inrush current: 11 A / 64 µs
- Permitted temperature range: M: -5...+35 °C, NM: 0...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.