System luminaires / Ball-impact and shock resistant safety luminaires / SN 8030.2

SN 8030.2 AP-06 AHB LED J/SV,RAL 9016 - (104418981)

Safety luminaire SN 8030.2AP-06 AHB LED J/SV  RAL 9016

Ball-impact and shock resistant LED safety luminaire with optimised light distribution for the illumination of escape routes. Powder-coated aluminium housing with slim design, perfect for use in environments with high mechanical stresses and in sports facilities.

Light distribution: Asymmetric High BayReference (Object) not found: tb89401039858023 escape routes. For mounting heights up to: 11,0 m. maximum 11,0 m luminaire spacing at 1 lx along the centre line of the escape route in accordance with EN 1838, taking into account a maintenance factor of 0.8

Ball-impact and shock resistant safety luminaires tested acc. to DIN VDE 0710-13.

Luminaires without testing acc. to DIN VDE 0710-13 as well as luminaires wih ball impact guards are not approved. According test certificates need to be added to the offer.

Impact strenght tested according to EN 50102.

 Luminaires without tests acc. to EN 50102 are not approved. According test certificates need to be added to the offer. 

The following characteristics need to be complied with:

LED-driver with integrated individual lamp monitoring for stand-by and continuous lighting without seperate BUS-line. Complying with international standards for safety and working, electromagnetic compatibility and interference resistance. LED output dimmable continuously in mains operation. For connection to JOKER-central battery systems.
Auswechselbares Betriebsgerät zur vereinfachten Wartung und Instandhaltung.

- Mounting type: ceiling mounting for exposed wiring
- Material: sheet steel powder-coated
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: replaceable 1 x 1,8W LED-module
- Light colour: 4000 K
- Light distribution: Asymmetric High Bay
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP40
- Protection class: I
- Impact resistance: IK10
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 16 mA
- Apparent power: 4,4 VA
- Inrush current: 8 A / 50 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.